| JOB SAFETY ANALYSIS | Job Task: Changing a 150 lb. Chlorine Gas Cylinder | Date: | Analysis Performed By: East Stroudsburg |
| --- | --- | --- | --- |
| SEQUENCE OF BASIC JOB STEPS | POTENTIAL HAZARDS | RECOMMENDED ACTION |
| 1. Turn on exhaust fan, open Cl2 room door and chain open. | Leaking Cl2 gas | Check Cl2 leak detector and smell |
| 2. Shut off empty Cl2 tank. | Rap knuckles | None observed |
| 3. Remove vacuum regulator from empty Cl2 tank and hang on support hook. | None | None observed |
| 4. Remove tank and store outside in empty storage area and make sure to chain empties back up. | Potential slip hazard during winter | Make sure path is clear to empty Cl2 storage |
| 5. Install new tank onto scale station And chain tank. | Potential back strain | Follow proper lifting and moving procedures |
| 6. Remove old lead seal ring and install new one on vacuum regulator. | None | None observed |
| 7. Install vacuum regulator to new Cl2 tank, tighten regulator bolt. | None | None observed |
| 8. Open slightly Cl2 valve and then close back up. Use ammonia vapor to check for any leaks at tank and regulator. | Dysfunctional value, dysfunctional seal allowing Cl2 gas to leaks | None observed |
| 9. Open Cl2 value by turning one half of a turn, switch vacuum regulator to reserve for automatic switch over so it will feed when other tank empties. Set scale at 150lbs. | Dysfunctional value, dysfunctional seal allowing Cl2 gas to leak | None observed |
| 10. Check installation, chain tank then exit by unchaining door, turning off fan and locking door. | None | None observed |